2

3

4

5

Installation Guide

Built in strainer

1

6

DSS-440S or DSS-420S

Normal filtration:-

- Valves 1, 2, 6 open

- Valves 3, 4, 5 closed

Strainer cleaning:-

- Valve 4 opens for  15 seconds

- Others remain

(recommended once a month)

Membrane flushing :-

- Valve 5 opens for @ 30 seconds

- Others remain

(recommended 2-4 times a week)

Backwash membrane cleaning:-

- Valves 1, 4, 6 closed

- Valves 2, 3, 5 opens till clean

(recommended once every 2-4 weeks or if the pressure drop significantly)

Above recommendations are subject to water quality and water usage

Incoming

water

Filtrate

(clean water)

To drain

To drain